## 工作表1
HH FSE - Rule-Based Engineering for MEP Main Trunk Auto-route AI
Item Ref | Category | Description of Rule | Remark
Z1 | Zoning | No MEP Main Trunk should be running "along" and "on" top of wall.
Z2 | Zoning | No MEP Main Trunk should running across MEP pipeduct.
Z3 | Zoning | No MEP Main Trunk should be running inside lift shaft
Z4 | Zoning | No MEP Main Trunk should be running inside lift motor room
Z5 | Zoning | No MEP Main Trunk should be running inside sttarcase
Z6 | Zoning | No MEP Main Trunk should be running under fire shutter of a fire zone
Z7 | Zoning | No MEP Main Trunk should be running under smoke curtain of a fire zone
Z8 | Zoning | Reserve 150mm clearance above false ceiling for lighting zone and sprinker heads tee-off piping
Z9 | Zoning | No MEP Main Trunk is allowed to run below access panel to Fire Damper unless a mininum clearance access of 350mm is maintained.
Z10 | Zoning | No MEP Main Trunk is allowed to run directly below supply air difusser or return air grilles.
Z11 | Zoning | No MEP Main Trunk is allowed to run directly below Fan Coil Unit ( FCU of MVAC Services) due to blockage of future access.
Z12 | Zoning | All MEP services installation leveling to use 10mm as a unit
Z13 | Zoning | All MEP services are minium 25mm below beam
Z14 | Zoning | All MEP services are minium 50mm below soffit
M1 | MVAC | Ratio of Depth to Width not to exceed 1 : 6
M2 | MVAC | The gap (horizontal spacing) between uninsulated ductwork are 75mm.
M3 | MVAC | The gap (horizontal spacing) between insulated ductwork are 125mm (If ductwork insulation is 25mm).
M4 | MVAC | The space (horizontal spacing) between wall/column and uninsulated ductwork are 75mm.
M5 | MVAC | The space (horizontal spacing) between wall/column and insulated ductwork are 100mm (If ductwork insulation is 25mm).
M6 | MVAC | 150mm Clearance(4 sides) of fire rated enclosure installation.
M7 | MVAC | The gap (all around) between insulated pipework are 150mm (If pipework insulation is 50mm).
M8 | MVAC | CHWP / HWP / CDWP installation space (For welding joint):
Equal or less than Dia.100 installation space min. 150mm (If pipework insulation is 50mm).
From Dia.200 to Dia.350 installation space min. 180mm (If pipework insulation is 50mm).
From Dia.400 to Dia.600 installation space min. 200mm (If pipework insulation is 50mm).
M9 | MVAC | CHWP / HWP / CDWP installation space (For coupling joint):
Equal or less than Dia.100 installation space min. 170mm (If pipework insulation is 50mm).
From Dia.200 to Dia.350 installation space min. 190mm (If pipework insulation is 50mm).
From Dia.400 to Dia.600 installation space min. 200mm (If pipework insulation is 50mm).
M10 | MVAC | CDP installation space (For Screw joint):
Equal or less than Dia.100 installation space min. 110mm. (If pipework insulation is 25mm)
From Dia.150 to Dia.200 installation space min. 140mm. (If pipework insulation is 25mm)
M11 | MVAC | Mininmum 1:100 gradient fall required for condensate drain pipe.
E1 | Electrical | 150mm Clearance on top of cable tray or trunking for cable laying
E2 | Electrical | 400mm clearance to be reserved on the side of cable tray or trunking for cable laying | I suggest to increase this figure to 450 to align with E7.
E3 | Electrical | Bending radius of electrical cable must beminimum 6 times the overall diameter of cable
E4 | Electrical | The gap (horizontal spacing) between cable tray or trunking are 50mm.
E5 | Electrical | The space (horizontal spacing) between wall/column and trunking/cable tray min. 75mm. |  | Table 1: Min Gradient Fall of Draina Pipe
E6 | Electrical | The space (horizontal spacing) between wall/column and cable ladder min. 100mm.
E7 | Electrical | Width of cable tray or trunking in group: |  | Pipe Diameter | Min. Fall
|  | Equal or less than 600mm at least 1 side maintenance space (450mm). |  | 100 mm & below | 1:40
|  | From 601mm to 1200mm at least 2 sides maintenance space (450mm). |  | 150mm to 200mm | 1: 70
E8 | Electrical | 150mm Clearance(4 sides) of fire rated enclosure installation. |  | 225mm to 250mm | 1: 100
E9 | Electrical | 300mm Clearance(4 sides) for busbar maintenance. |  | 300mm to 350mm | 1: 150
|  |  |  | 400 mm & above | 1: 200
PD1 | Plumbing & Drainage | Mininmum gradient fall required for drainage and waste pipes shall refer to Table 1
PD2 | Plumbing & Drainage | Drainge vent pipe must inclined upward at minimum of 1:100 gradient
PD3 | Plumbing & Drainage | No setting up towards direction of fall allowed
PD4 | Plumbing & Drainage | No piping running inside any electrical room such as L.V. switch room, server room, ELV room & UPS room etc.
PD5 | Plumbing & Drainage | No water piping running directly on top of electrical panel that belongs to any MEP Services
PD6 | Plumbing & Drainage | No water piping running on top and along of electrical trunkings & busbar. However, crossing over is allowed.
PD7 | Plumbing & Drainage | No horizontal run of drainage pipe to exceed 30m
PD8 | Plumbing & Drainage | No drainage pipe to be running directly on top of car parking space of car parking area
PD9 | Plumbing & Drainage | The installation space of drainage trap min. 400mm height + 100 maintenance underneath.
PD10 | Plumbing & Drainage | Potable water installation space (For copper welding joint)
Equal or less than Dia.50 installation space min. 60mm.
From Dia.80 to Dia.100 installation space min. 90mm.
PD11 | Plumbing & Drainage | HWP installation space (For copper welding joint)
Equal or less than Dia.50 installation space min. 110mm. (If pipework insulation is 25mm)
From Dia.80 to Dia.100 installation space min. 140mm. (If pipework insulation is 25mm)
PD11 | Plumbing & Drainage | Ductile Iron pipe installation space (For flange joint)
Equal or less than Dia.100 installation space min. 150mm.
From Dia.150 to Dia.200 installation space min. 200mm.
PD12 | Plumbing & Drainage | Cast Iron Pipe installation space (Foor SWP/WP/RWP/VP)
Equal or less than Dia.100 installation space min. 50mm.
From Dia.150 to Dia.300 installation space min. 60mm.
From Dia.350 to Dia.500 installation space min. 60mm.
F1 | Fire | No MEP Main Trunk should be running directly below smoke detector or heat detector located inside ceiling void unless a clearance of 400mm is maintained for servicing
Abbreviation:
MEP | Mechanical, electrical, Plumbing & drainage installations
CHWP | Chilled Water Pipe
HWP | How Water Pipe
CDWP | Condensate Water Pipe
CDP | Condensate Drain Pipe
SWP | Soil Water Pipe
WP | Waste Ppipe
RWP | Rain Water Pipe
VP | Vent Pipe